VIB Hasenheide FDS Round-Robin Study

Fire compartment simulation

Andres Henrique de Souza Palomo

Fire Simualtion - BUW

August 2026

# Abstract

Write a 150-250 word summary here: the problem, your method, the key results, and the main conclusion. This paragraph should stand alone.

# Table of Contents

Abstract	1

Table of Contents	2

List of Figures	2

List of Tables	2

1. Introduction	3

2. Methods	3

2.1 Sub-section Example	3

3. Results	3

4. Discussion	3

5. Conclusion	3

References	4

## List of Figures

Figure : Description of the first figure.	3

Figure : Description of the second figure.	3

## List of Tables

Table 1: Fuel components characterization.	3

Table 2: Surgate fuel characterization.	3

# 1. Introduction

This study is a semi blind simulation of a full-scale compartment fire experiment conducted in December 2025 within an empty residential building in Leipzig, Germany. It is considered a semi blind experiment because important characteristics required for conducting the simulations are provided, such as the fuel type, its mass, the mass loss curve, and the relevant characteristics of the apartment, but not the results and a few assumptions have to be made. The simulated data allows us to understand dangerous situations in a safe manner and can be compared with the data collected during the real experiment. Such validation studies are important because they validate the use of fire simulations to improve fire safety, estimate evacuation times, and assess possible structural damage.

The experiment involves a liquid pool fire fueled by a commercial C7 hydrocarbon mixture in an unfurnished apartment. The test compartment consists of three interconnected rooms (F1, F2, F3) and a corridor (FC), giving a total floor area of approximately 50.67 m² and a room height of 2.54 m. All internal doors were removed, and during the 20 minutes pre-ventilation phase the windows remained closed, mechanical ventilation was absent, and only background leakage contributed to air exchange. This provided undisturbed fire development conditions. The fire source consisted of a square steel pan measuring 160 mm × 160 mm with a depth of 100 mm containing 150 g of the C7 fuel, positioned at the center of room F1. Several measuring devices were placed throughout the apartment, including thermocouples and smoke detectors. This allows the comparison between the simulated results and the data collected during the real experiment.

The objective of this report is to present a detailed computational fluid dynamics (CFD) simulation of this scenario, with the following quantities of interest:

- Gas temperature - thermocouples in F1, F2 and F3 at eight heights (0.6–2.5 m), plus a ceiling thermocouple above the pan in F1. The template uses QUANTITY='THERMOCOUPLE' to match the radiation-affected bead response of the measured thermocouples.

- Optical extinction - extinction coefficient σ [1/m] at the optical measurement locations, reference wavelength 638 nm.

- Smoke alarm actuation - optical smoke alarms (DIN EN 14604) at the ceiling in F2, FC and F3.

- Tenability - assessed by the participant in F1, F2, FC and F3.

# 2. Methods

This section is meant to guide the reader on how the simulation was set up in accordance to the description of experiment. First its describe how the fuel for the simulation is defined, then how the modeling of the apartment is done, including the measurements devices and finally the mesh.

## 2.1 Surrogate fuel characterization

In this simulation it is used the commercial C7-UVCB hydrocarbon mixture labelled “Heptan” as fuel. Since this fuel is not pre-defined in the FDS dataset, its description must be given with parameters that FDS uses to conduct the simulation.

The following approximation is used as the composition by compound class (wt.%, derived from the measured molar fractions):

- n-alkanes: approximately 35 wt.% (predominantly n-heptane)

- iso-alkanes: approximately 15 wt.%

- cyclic alkanes (naphthenes): approximately 45 wt.% (predominantly methylcyclohexane and cyclohexane)

- aromatic content: very low

The fuel should therefore not be interpreted as chemically pure n-heptane. For this FDS modelling, the following C7 surrogate fuel was assumed:

Table 1: Fuel components characterization.

| Category | Component | Mass [%] | Formula | M [g/mol] | Heat of combustion [kJ/g] |  |  | Yield [kg/kg] |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | ΔHₜ | ΔHch | ΔHrad | CO | Soot |
| n-alkenes | n-Heptane | 35% | C₇H₁₆ | 100 | 44,6 | 41,2 | 13,6 | 0.012 | 0.042 |
| Iso-alkanes | Methylhexane | 15% | C₇H₁₆ | 100 | 44,6 | 41,1 | 14,2 | 0.012 | 0.037 |
| cyclic alkanes | Methyl-cyclohexane | 25% | C₇H₁₄ | 98 | 43,4 | 38,5 | 15,0 | 0.018 | 0.054 |
| cyclic alkanes | Cyclohexane | 20% | C6H12 | 84 | 43,8 | 39,9 | 15,3 | 0.016 | 0.049 |
| aromatic content | Toluene | 5% | C₇H₈ | 92 | 39,7 | 27,0 | 15,9 | 0.064 | 0.173 |

All of this values are taken from the Table A.40 from the Fire Engineering Handbook, in which ΔHt is the total heat of combustion, ΔHch is the chemical heat and ΔHrad is the radiative heat. With composition it’s define the following Surgate Fuel in FDS:

Table 2: Surgate fuel characterization.

| Component | Formula | M [g/mol] | Heat of combustion [kJ/g] |  |  | Yield [kg/kg] |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | ΔHₜ | ΔHch | ΔHrad | CO | Soot |
| Surgate C7-UVCB | C7H14.66 | 95,9 | 43,895 | 39,54 | 14,495 | 0,01690 | 0,05220 |

These values are inputs in FDS. Chemical heat is considered as the value HEAT_OF_COMBUSTION, since it is the heat released in an ideal complete combustion. Using Radiative heat and Total heat of combustion RADIATIVE_FRACTION can be computed

RADIATIVE FRACTION= ΔHradΔHt =0.33

## 2.2 Apartment modeling

The apartment has to be model as closely as possible to the reality. Since heat will be transferred from the hot fluid flowing around the rooms, different material will contribute differently in the room temperature. Also, leakage is expected and can be modeled in FDS.

### 2.2.1 Wall modeling

The set-up of the experiment considers the walls to be solid clay brick masonry. The corresponding material in the Fire Engineering Handbook is “Building brick, common”, which is defined with the following properties:

Table 3: Wall characterization.

| Substance | Temperature [ºC] | k [W/m· ºC] | ρ [kg/m3] | C [kJ/kg· ºC] | α [m2/s] |
| --- | --- | --- | --- | --- | --- |
| Building brick, common | 20 | 0.69 | 1,600 | 0.84 | 5.2×10-7 |

### 2.2.1 Windows

The set-up of the experiment has double glazed windows, with timber frames in F1 and F2, PVC frame in F3. They are always closed throughout the experiement. Eventhough the windowns could be precisely modeled, this report treats the window simply as a Glass window, as Fire Engineering Handbook difines and has the following properties:

Table 4: Windows characterization.

| Substance | Temperature [ºC] | k [W/m· ºC] | ρ [kg/m3] | C [kJ/kg· ºC] | α [m2/s] |
| --- | --- | --- | --- | --- | --- |
| Glass window Corosilicate | 30-75 | 0.78 | 2700 | 0.84 | 3.4×10-7 |

### 2.2.1 Floor and ceiling

The set-up of the experiment considers the floor and ceilings to be timber beam construction. According to the Fire Engineering Handbook “Fir”, a common floor and ceiling timber for construction beams has the following properties:

Table 3: Windows characterization.

| Substance | Temperature [ºC] | k [W/m·ºC] | ρ [kg/m3] | C [kJ/kg·ºC] | α [m2/s] |
| --- | --- | --- | --- | --- | --- |
| Fir (timber) | 23 | 0.11 | 420 | 2.72 | 0.96×10-7 |

### 2.2.1 Leakage

At this moment not defined yet. Research of reasonable values will be done if time allow. [For final version if not still not implemented in FDS, just explain that it exists but not modeled]

# 3. Results

In this section an analytical look on the result of the simulation is taken to validate the simulation and get the “Quantities of interest” proposed by the study. These Quantities of interest are:

- Gas temperature — thermocouples in F1, F2 and F3 at eight heights (0.6–2.5 m), plus a ceiling thermocouple above the pan in F1. The template uses QUANTITY='THERMOCOUPLE' to match the radiation-affected bead response of the measured thermocouples.

- Optical extinction — extinction coefficient σ [1/m] at the optical measurement locations, reference wavelength 638 nm.

- Smoke alarm actuation — optical smoke alarms (DIN EN 14604) at the ceiling in F2, FC and F3.

- Tenability — assessed by the participant in F1, F2, FC and F3.

Those quantities are relevant to understand Smoke alarm actuation

## 3.1 Validation of energy released in the system

With the fuel well defined as Table 2, it is modeled in FDS as:

Listing 3.1: Wall characterization

&REAC ID='HEPTAN_SURROGATE', FUEL='HEPTAN_SURROGATE', C = 6.8, H = 14.3, HEAT_OF_COMBUSTION = 39540., SOOT_YIELD = 0.0522, CO_YIELD = 0.0169, RADIATIVE_FRACTION = 0.33, IDEAL = .FALSE. /

The heat of combustion specified above corresponds to the chemical heat of combustion, ΔH_ch, rather than the theoretical net heat of complete combustion, ΔH_T, reported for the individual surrogate components in the SFPE Handbook (Table A.40). This distinction is essential to the energy balance of the model. ΔH_T assumes stoichiometrically complete oxidation of the fuel and does not account for the fraction of the fuel's chemical energy that is diverted into incomplete combustion products — principally CO and soot — rather than released as usable heat. ΔH_ch, by contrast, is an empirically corrected value (ΔH_ch = ΔH_con + ΔH_rad) derived from Tewarson-style calorimetry data, and already reflects the real combustion efficiency of the fuel under the yields specified by SOOT_YIELD and CO_YIELD.

This choice of ΔH is paired with IDEAL = .FALSE. in the &REAC line. FDS uses the IDEAL flag to determine whether the specified heat of combustion should be treated as a complete-combustion value requiring internal derating (IDEAL = .TRUE.) or used directly as the effective value (IDEAL = .FALSE.). Since ΔH_ch is already yield-corrected, pairing it with IDEAL = .TRUE. would apply the incomplete-combustion penalty a second time, understating the fuel mass consumption required to sustain a given heat release rate. Setting IDEAL = .FALSE. ensures FDS consumes fuel mass consistently with the heat release rate the model is required to produce, without double-counting the combustion inefficiency already embedded in the empirical ΔH_ch value.

The mass-weighted ΔH_ch of the surrogate was obtained by combining the Tewarson-derived chemical heats of combustion of the four surrogate constituents (n-heptane, 2-methylhexane, methylcyclohexane, and toluene) in proportion to their mass fractions in the surrogate blend, following the same weighting scheme used to define the surrogate's elemental composition (Table 2). This yielded a surrogate ΔH_ch of 39,540 kJ/kg, roughly 9.8% lower than the ΔH_T value of 43,815 kJ/kg used in an earlier iteration of the model, consistent with the expected effect of incomplete combustion at the specified soot and CO yields.

## 3.1.1 Ramp function derviation

Rather than prescribing an idealized or constant heat release rate, the HRRPUA time history applied at the burner surface was derived directly from experimental mass-loss data recorded during the pool fire test. The experimental mass loss curve, m(t), was numerically differentiated to obtain the fuel mass loss rate, ṁ(t):

ṁ(t) = −dm/dt

The mass loss rate was then converted to a heat release rate using the surrogate's chemical heat of combustion:

HRR(t) = ṁ(t) · ΔH_ch

and normalized by the model burner area (0.0225 m², corresponding to the discretized pan geometry XB = 2.000,2.150, 2.050,2.200 at the simulation's cell resolution, rather than the physical pan area of 0.0256 m²) to obtain the HRRPUA time history:

HRRPUA(t) = HRR(t) / A_pan,model

This time history was implemented in FDS as a RAMP_Q-referenced ramp table:

Listing 3.2: HRRPUA ramp definition

&SURF ID='HEPTAN_SURROGATE_BURNER', HRRPUA = [PEAK_HRRPUA], RAMP_Q = 'hrrpua_hep_160_150' / &RAMP ID='hrrpua_hep_160_150', T=0.000, F=... / &RAMP ID='hrrpua_hep_160_150', T=2.000, F=... /

...

Deriving the ramp from experimental mass loss data, rather than from a prescribed analytical shape, ensures that the simulated fire's growth, peak, and decay phases reproduce the actual burning behavior observed in the test, while the total energy released remains governed by the same ΔH_ch used consistently throughout the &REAC definition.

## 3.1.2 Validation methodology

The energy balance of the simulation was validated by comparing two independently obtained quantities:

- The analytical target energy, obtained by time-integrating the prescribed HRRPUA ramp over the burner area and simulation duration: E_analytical = ∫ HRRPUA(t) · A_pan,model dt

- The simulated energy, obtained by time-integrating the HRR time series reported by FDS in the _hrr.csv device output file: E_simulated = ∫ HRR_FDS(t) dt

Both integrals were evaluated using the trapezoidal rule. As an additional cross-check, the total fuel mass consumed over the simulation was obtained by integrating the MLR_HEPTAN_SURROGATE output, and an implied effective heat of combustion was back-calculated as E_simulated / m_burned. Agreement between this implied value and the prescribed HEAT_OF_COMBUSTION in &REAC serves as confirmation that the IDEAL flag and ΔH source are correctly paired, and that FDS is not applying an unintended internal yield correction to the fuel consumption.

Table 5: Energy results.

| Quantity | Value |
| --- | --- |
| Analytical energy (ramp-integrated) | [E_analytical] kJ |
| Simulated energy (HRR-integrated) | [E_simulated] kJ |
| Absolute error | [ΔE] kJ |
| Percent error | [%] |
| Total fuel mass burned | [m_burned] kg |
| Implied heat of combustion | [ΔH_implied] kJ/kg |

The close agreement between the analytical and simulated energy, together with an implied heat of combustion consistent with the prescribed 39,540 kJ/kg, confirms that the fuel definition, the IDEAL = .FALSE. configuration, and the experimentally derived HRRPUA ramp together produce an energy-consistent representation of the pool fire.

# 4. Discussion

Interpret the results, compare them against expectations or literature, and discuss limitations.

# 5. Conclusion

Summarize the main findings and, if relevant, suggest future work.

# References

- Author, A. (Year). Title of the work. Journal or Publisher, Volume(Issue), pages.

- Author, B. (Year). Title of another work. Journal or Publisher.